## Revs
REVISION CONTROL
<< SITE NAME >>
Physical I.O. Spreadsheet
Version | Date | Author | Comment
0.3 | 2016-10-28 | James Morrison | 30 % Design - Issued for Client Comment
0.31 | 2016-11-18 | James Morrison | 30 % Design - Modified Site Option IDs, Pump Naming
0.6 | 2017-02-14 | James Morrison | 60 % Design - Modified to align with electrical drawings for
0.61 | 2017-02-28 | James Morrison | 60 % Design - Working following Review
0.62 | 2017-02-28 | James Morrison | 60 % Design - Working following Review
0.63 | 2017-03-02 | Alex Witthoft | 60 % Design - Highlighted IO inconsistencies (dwgs & spec needs to align with blue fields)
0.64 | 2017-03-02 | James Morrison | 60 % Design - Updated RTU Tag Names, 24VDC Power supply point descriptions.
0.65 | 2017-03-27 | Alex Witthoft | 60 % Design - Added Options D1 and D2 (Mandatory Pumps 1 & 2)
1 | 2017-04-04 | Alex Witthoft | 100% Design - Issued for Programming of Standard Code
1.1 | 2017-05-16 | Alex Witthoft | Added Safety Function Healthy Output - DO1, Modified All Stops to be Emergency Stop
1.2 | 2017-06-15 | James Morrison | Modified Site Options, Removed Control Mode DI.
1.21 | 2017-09-27 | James Morrison | Updated RTU and Expansion Module Model Numbers
2 | 2017-11-24 | James Morrison | Revved up for release with Functional Spec v3.0
2.01 | 2018-04-03 | James Morrison | Fixed Pump Options Logic on DI1 Tab
3 | 2018-09-12 | James Morrison | Updated to align with Standard Functional Specification v6.0
| Option | Active | Detail
| - | Y | STANDARD
| ^ | Y | SPARE IO CHANNEL
| A | Y | Auto Transfer Switch & Generator
| B | Y | CT Metering
| C | Y | SCADAPack RTU
| D1 | Y | Pump 3 Installed
| D2 | Y | Pump 4 Installed
| D3 | Y | Pump 5 Installed
| D4 | Y | Pilot Pump Installed
| E1 | Y | Discharge Flowmeter Installed
| E2 | Y | Bypass Flowmeter Installed
| E3 | Y | Redundant Discharge Pressure Transmitter Installed
| F | Y | Trio Radio
| G | Y | 3G Modem
| H | Y | PSTN Modem
| I | Y | Fire Mode Switch
| J | N | Card Reader (NOT USED)
| K1 | Y | Pump Box Sump Pump
| K2 | Y | Flow Meter Pit Sump Pump
| L1 | Y | Pump Box Sump Pit Level Probe
| L2 | Y | Flow Meter Pit Level Probe
| M | Y | Pump Box Ventilation Fan
| N | Y | Area Lighting
| O | Y | Dual 24VDC Power Supplies
| P | Y | Power Meter
| U | Y | Emergency Stop Installed
| V | Y | Emergency Stop Safety Function Failure Monitoring

## Rack Layout
RTU IO ALLOCATION
<< SITE NAME >>
Physical I.O. Spreadsheet
RTU: | TBUP535‐EA56‐AB10S |  | SCADAPack 535E - 6 Analog Inputs shipped selectable as 0-20mA or 4-20mA, 16 Digital Inputs (12/24V) and 8 Dry Contact Relay outputs (6 Form A, 2 Form C), 2 channel Analog Output option, shipped selectable as 0-20 mA or 4-20mA, external DC supply
Expansion Module: | TBUX297585S |  | Model 6601-20mA, 16 D/I 12-24 volts, 8 Dry Contact Relay outputs (6 Form A, 2 Form C) , 6 config. A/I (0/4-20mA), 2 A/O (external DC supply)
TBUP535‐EA56‐AB10S
TBUX297585S

## DI1
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Digital Inputs - Onboard RTU
| I/O # | Term | Tag | Description | Off State | On State | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
16 | DI01 | DI 1 | stn1EStopHealthy | Station Emergency Stop Healthy | Fault | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI02 | DI 2 | stn1EnergexPwr | Energex Power Healthy | Off | On |  |  |  |  | - |  |  |  | Y
14 | DI03 | DI 3 | stn1mainsPower | Station Mains Power Healthy | Off | On |  |  |  |  | - |  |  |  | Y
14 | DI04 | DI 4 | stn1surgeDivOK | Surge diverter and Filter OK | Fault | Healthy |  |  |  |  | - |  |  |  | Y
13 | DI05 | DI 5 | psu1batteryOK | PS1 Battery OK | Fault | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI06 | DI 6 | psu1powerOK | PS1 Power On | Fault | Healthy |  |  |  |  | - |  |  |  | Y
11 | DI07 | DI 7 | stn1DoorsClsed | Station Doors Closed | Alarm | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI08 | DI 8 | stn1RemoteMode | Station Remote Mode | Local | Remote |  |  |  |  | - |  |  |  | Y
9 | DI09 | DI 9 | stn1MPCOK | MPC Healthy | Fault | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI10 | DI 10 | pmp1VFDHealthy | Pump 1 Healthy | Fault | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI11 | DI 11 | pmp2VFDHealthy | Pump 2 Healthy | Fault | Healthy |  |  |  |  | - |  |  |  | Y
14 | DI12 | DI 12 | pmp3VFDHealthy | Pump 3 Healthy | Fault | Healthy |  |  |  |  | D1 |  |  |  | Y
14 | DI13 | DI 13 | pmp4VFDHealthy | Pump 4 Healthy | Fault | Healthy |  |  |  |  | D2 |  |  |  | Y
14 | DI14 | DI 14 | pmp5VFDHealthy | Pump 5 Healthy | Fault | Healthy |  |  |  |  | D3 |  |  |  | Y
12 | DI15 | DI 15 | stn1FireMode | Fire Mode Selected | Off | Fire Mode |  |  |  |  | I |  |  |  | Y
14 | DI16 | DI 16 | pmpPVFDHealthy | Pilot Pump Healthy | Fault | Healthy |  |  |  |  | D4 |  |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /

## DO1
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Digital Outputs - Onboard RTU
| I/O # | Term | Tag | Description | Off State | On State | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
12 | DO01 | DO 1 | gen1Exercise | Generator Exercise Relay | Disable | Enable |  |  |  |  | A |  |  |  | Y
13 | DO02 | DO 2 | stn1ElectTest | Electrode Test Relay | Disable | Enable |  |  |  |  | L1 |  |  |  | Y
15 | DO03 | DO 3 | stn1SafetyFault | Safety Function Fault Indication Lamp | Disable | Enable |  |  |  |  | V |  |  |  | Y
1 | DO04 | DO 4 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | DO05 | DO 5 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | DO06 | DO 6 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | DO07 | DO 7 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | DO08 | DO 8 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /

## AI-AO1
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Analog Inputs & Outputs - Onboard RTU
| I/O # | Term | Tag | Description | 4mA | 20mA | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
13 | AI01 | AI 1+, AI 1- | flw1rawSignal | Delivery flowmeter (raw signal) | 0.00 l/s | ??? l/s |  |  |  |  | E1 |  |  |  | Y
13 | AI02 | AI 2+, AI 2- | flw2rawSignal | Bypass flowmeter (raw signal) | 0.00 l/s | ??? l/s |  |  |  |  | E2 |  |  |  | Y
13 | AI03 | AI 3+, AI 3- | pre1rawSignal | Suction pressure (raw signal) | 0.00 m | ??? m |  |  |  |  | - |  |  |  | Y
13 | AI04 | AI 4+, AI 4- | pre2rawSignal | Main Delivery pressure (raw signal) | 0.00 m | ??? m |  |  |  |  | - |  |  |  | Y
13 | AI05 | AI 5+, AI 5- | lvl1rawSignal | Generator fuel level (raw signal) | ??? | ??? |  |  |  |  | A |  |  |  | Y
13 | AI06 | AI 6+, AI 6- | pre2rawSignal | Backup Delivery pressure (raw signal) | 0.00 m | ??? m |  |  |  |  | E3 |  |  |  | Y
| I/O # | Term | Tag | Description | 4mA | 20mA | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
| AO1 | AO 1 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
| AO2 | AO 2 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /

## DI2
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Digital Inputs - Expansion Module
| I/O # | Term | Tag | Description | Off State | On State | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
14 | DI17 | DI 1 | stn1ATSNormPos | Transfer Switch Normal Position | Off | Normal |  |  |  |  | - |  |  |  | Y
9 | DI18 | DI 2 | gen1fault | Generator Fault | Healthy | Fault |  |  |  |  | A |  |  |  | Y
11 | DI19 | DI 3 | gen1warning | Generator Warning | Healthy | Warning |  |  |  |  | A |  |  |  | Y
11 | DI20 | DI 4 | gen1lowFuel | Generator Low Fuel | Off | Low Fuel |  |  |  |  | A |  |  |  | Y
11 | DI21 | DI 5 | gen1medFuel | Generator Medium Fuel | Off | Medium Fuel |  |  |  |  | A |  |  |  | Y
14 | DI22 | DI 6 | gen1Running | Generator Running | Off | Running |  |  |  |  | A |  |  |  | Y
11 | DI23 | DI 7 | gen1CanopyClsd | Generator Canopy Doors Closed | Door Open | All Doors Closed |  |  |  |  | A | Closed = On? |  |  | Y
13 | DI24 | DI 8 | gen1CBsClosed | Generator CBs Closed | CB Open | All CBs closed |  |  |  |  | A |  |  |  | Y
14 | DI25 | DI 9 | stn1genATSAuto | Generator and ATS in Auto | Gen/ATS not Auto | Both in Auto |  |  |  |  | A |  |  |  | Y
10 | DI26 | DI 10 | gen1onSite | Generator On Site | Not On Site | On Site |  |  |  |  | A |  |  |  | Y
1 | DI27 | DI 11 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | DI28 | DI 12 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
11 | DI29 | DI 13 | pit1flooded | Pump Box Pit Flooded | Healthy | Flooded |  |  |  |  | L1 |  |  |  | Y
11 | DI30 | DI 14 | pit1probeOK | Pump Box Pit Probe Healthy | Fault | Healthy |  |  |  |  | L1 |  |  |  | Y
11 | DI31 | DI 15 | pit2flooded | Flow Meter Pit Flooded | Healthy | Flooded |  |  |  |  | L2 |  |  |  | Y
11 | DI32 | DI 16 | pit2probeOK | Flow Meter Pit Probe Healthy | Fault | Healthy |  |  |  |  | L2 |  |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /

## DO2
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Digital Outputs - Expansion Module
| I/O # | Term | Tag | Description | Off State | On State | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
1 | DO09 | DO 1 | - | Spare | - | - |  |  |  |  | ^ | Form C (NO/NC) |  |  | Y
1 | DO10 | DO 2 | - | Spare | - | - |  |  |  |  | ^ | Form C (NO/NC) |  |  | Y
1 | DO11 | DO 3 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
1 | DO12 | DO 4 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
1 | DO13 | DO 5 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
1 | DO14 | DO 6 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
1 | DO15 | DO 7 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
1 | DO16 | DO 8 | - | Spare | - | - |  |  |  |  | ^ | Form A (NO) |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /

## AI-AO2
<< SITE NAME >>
|  |  |  | Physical I.O. Spreadsheet | Analog Inputs & Outputs - Expansion Module
| I/O # | Term | Tag | Description | 4mA | 20mA | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
1 | AI07 | AI 1+, AI 1- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | AI08 | AI 2+, AI 2- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | AI09 | AI 3+, AI 3- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | AI10 | AI 4+, AI 4- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | AI11 | AI 5+, AI 5- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
1 | AI12 | AI 6+, AI 6- | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
| I/O # | Term | Tag | Description | 4mA | 20mA | Term. # | Wire # | Schem | Term | O | Comment | FAT | SAT
| AO3 | AO 1 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
| AO4 | AO 2 | - | Spare | - | - |  |  |  |  | ^ |  |  |  | Y
|  |  |  | FACTORY ACCEPTANCE TESTED BY: |  | Date | / /
|  |  |  | SITE ACCEPTANCE TESTED BY: |  | Date | / /